## LOG SHEET
S.NO. | FEEDER NAME | ID | S.NO. | FEEDER NAME | ID
1 | BIRONDI | FHBRSWF006 | 41 | EXPRESSWAY | FHKPR2F002
2 | JAITPUR | FHBRSWF004 | 42 | Haldona | FHKPR2F020
3 | Chuharpur Khadar | FHCHI4F002 | 43 | BZP | FHLKNWF004
4 | Momnathal | FHCHI4F006 | 44 | Doob Area | FHLKNWF018
5 | SANTOSH NAGAR | FHCONRF004 | 45 | KULESRA | FHLKNWF014
6 | TILAPTA CANAL | FHCONRF016 | 46 | LAKHNAWLI | FHLKNWF008
7 | Navada (Urban) | FHDEL1F008 | 47 | MALAKPUR | FHDMASF016
8 | DADHA VILLAGE | FHECEXF008 | 48 | Suthyana | FHLKNWF012
9 | DADHA | FHECTCF004 | 49 | IMALIYAKA | FHLKSRF014
10 | KHANPUR | FHECTCF014 | 50 | MADHAIYA | FHST36F012
11 | GHANGHOLA | FHEC11F006 | 51 | AICHAR | FHST37F008
12 | LADPURA | FHEC11F008 | 52 | MATHURAPUR | FHST37F026
13 | MAICHA | FHEC11F010 | 53 | DEVLA | FHSITBF002
14 | NALAGARHA | FHECT2F012 | 54 | Gulistanpur | FHSCSWF004
15 | TUBEWELL BRANCH | FHECT2F002 | 55 | DADRI ROAD TILAPTA | FHSCSWF020
16 | KASNA 6% ABADI | FHECT6F018 | 56 | KHODNAKHURD | FHSNPRF006
17 | Kasna Village | FHECT6F022 | 57 | SAINI | FHSNPRF008
18 | Khera Chauganpur | FHSW10F006 | 58 | SWARAJPUR | FHSNPRF002
19 | KHERPUR GUJJAR | FHSW02F008 | 59 | VEDPURA | FHSNPRF020
20 | TUSYANA | FHESS6F002 | 60 | BHANOTA | FHSNPRF024
21 | SAKIPUR | FHETAAF006 | 61 | SUNPURA | FHSNPRF026
22 | C.M Market | FHGMA1F006 | 62 | BHAGAT SINGH SCHOOL | FHSRJPF030
23 | BILASPUR TOWN | FHGDHRF028 | 63 | Lotus Park | FHSRJPF018
24 | GIRIDHARPUR | FHGDHRF016 | 64 | SURAJPUR A & D POCKET | FHSRJPF014
25 | KHERLI HAFIZPUR | FHGDHRF022 | 65 | Surajpur Market | FHSRJPF022
26 | PANCHAYTAN | FHGDHRF024 | 66 | BARAHI MANDIR | FHSRJPF032
27 | PATLAKHERA PTW | FHGDHRF026 | 67 | KASHI RAM | FHXU01F002
28 | ROUNI | FHGDHRF020 | 68 | GHORI BHACHERA | FHXU01F010
29 | BULANDKHERA | FHHTWAF004 | 69 | JUNPAT | FHXU01F012
30 | DALELGARH | FHHTWAF006 | 70 | DABRA | FHXU03F008
31 | JHALDA | FHHTWAF014 | 71 | RITHORI | FHXU03F002
32 | KANARSI | FHHTWAF002 | 72 | DLF SCHOOL | FHZET1F014
33 | NAWADA | FHHTWAF008 | 73 | MAKORA | FHZET1F004
34 | BISRAKH BLOCK | FHJLPRF028 | 74 | MOTIPUR | FHITCTF014
35 | AIMNABAD | FHJLPRF032 | 75 | GHARBARA VILLAGE | FHITCTF016
36 | Habibpur | FHJLPRF024 | 76 | Murshadpur | FHITCTF018
37 | HALDAUNI | FHJLPRF030 | 77 | KULESRA COLONY | FHLKNWF022
38 | JALPURA | FHJLPRF002 | 78 | BHUDHA ROAD COLONY | FHSCSWF018
39 | Tata Motors | FHJLPRF012 | 79 | ATAI MURADPUR | FHLKSRF016
40 | TUGALPUR MARKET | FHKPR1F004 | 80 | POVARI | FHLKSRF018
Note on B9: eco-1 ext-1 s/s

## Help Sheet
S.NO. | FEEDER NAME | FEEDER ID | S.NO. | FEEDER NAME | FEEDER ID | S.NO. | FEEDER NAME | FEEDER ID
1 | BIRONDI | FHBRSWF006 | 1 | BIRONDI | FHBRSWF006 | 1 | BIRONDI | FHBRSWF006
2 | JAITPUR | FHBRSWF004 | 2 | JAITPUR | FHBRSWF004 | 2 | JAITPUR | FHBRSWF004
3 | Chuharpur Khadar | FHCHI4F002 | 3 | Chuharpur Khadar | FHCHI4F002 | 3 | Chuharpur Khadar | FHCHI4F002
4 | Momnathal | FHCHI4F006 | 4 | Momnathal | FHCHI4F006 | 4 | Momnathal | FHCHI4F006
5 | SANTOSH NAGAR | FHCONRF004 | 5 | SANTOSH NAGAR | FHCONRF004 | 5 | SANTOSH NAGAR | FHCONRF004
6 | TILAPTA CANAL | FHCONRF016 | 6 | TILAPTA CANAL | FHCONRF016 | 6 | TILAPTA CANAL | FHCONRF016
7 | Navada (Urban) | FHDEL1F008 | 7 | Navada (Urban) | FHDEL1F008 | 7 | Navada (Urban) | FHDEL1F008
8 | DADHA VILLAGE | FHECEXF008 | 8 | DADHA VILLAGE | FHECEXF008 | 8 | DADHA VILLAGE | FHECEXF008
9 | DADHA | FHECTCF004 | 9 | DADHA | FHECTCF004 | 9 | DADHA | FHECTCF004
10 | KHANPUR | FHECTCF014 | 10 | KHANPUR | FHECTCF014 | 10 | KHANPUR | FHECTCF014
11 | GHANGHOLA | FHEC11F006 | 11 | GHANGHOLA | FHEC11F006 | 11 | GHANGHOLA | FHEC11F006
12 | LADPURA | FHEC11F008 | 12 | LADPURA | FHEC11F008 | 12 | LADPURA | FHEC11F008
13 | MAICHA | FHEC11F010 | 13 | MAICHA | FHEC11F010 | 13 | MAICHA | FHEC11F010
14 | NALAGARHA | FHECT2F012 | 14 | NALAGARHA | FHECT2F012 | 14 | NALAGARHA | FHECT2F012
15 | TUBEWELL BRANCH | FHECT2F002 | 15 | TUBEWELL BRANCH | FHECT2F002 | 15 | TUBEWELL BRANCH | FHECT2F002
16 | KASNA 6% ABADI | FHECT6F018 | 16 | KASNA 6% ABADI | FHECT6F018 | 16 | KASNA 6% ABADI | FHECT6F018
17 | Kasna Village | FHECT6F022 | 17 | Kasna Village | FHECT6F022 | 17 | Kasna Village | FHECT6F022
18 | Khera Chauganpur | FHSW10F006 | 18 | Khera Chauganpur | FHSW10F006 | 18 | Khera Chauganpur | FHSW10F006
19 | KHERPUR GUJJAR | FHSW02F008 | 19 | KHERPUR GUJJAR | FHSW02F008 | 19 | KHERPUR GUJJAR | FHSW02F008
20 | TUSYANA | FHESS6F002 | 20 | TUSYANA | FHESS6F002 | 20 | TUSYANA | FHESS6F002
21 | SAKIPUR | FHETAAF006 | 21 | SAKIPUR | FHETAAF006 | 21 | SAKIPUR | FHETAAF006
22 | C.M Market | FHGMA1F006 | 22 | C.M Market | FHGMA1F006 | 22 | C.M Market | FHGMA1F006
23 | BILASPUR TOWN | FHGDHRF028 | 23 | BILASPUR TOWN | FHGDHRF028 | 23 | BILASPUR TOWN | FHGDHRF028
24 | GIRIDHARPUR | FHGDHRF016 | 24 | GIRIDHARPUR | FHGDHRF016 | 24 | GIRIDHARPUR | FHGDHRF016
25 | KHERLI HAFIZPUR | FHGDHRF022 | 25 | KHERLI HAFIZPUR | FHGDHRF022 | 25 | KHERLI HAFIZPUR | FHGDHRF022
26 | PANCHAYTAN | FHGDHRF024 | 26 | PANCHAYTAN | FHGDHRF024 | 26 | PANCHAYTAN | FHGDHRF024
27 | PATLAKHERA PTW | FHGDHRF026 | 27 | PATLAKHERA PTW | FHGDHRF026 | 27 | PATLAKHERA PTW | FHGDHRF026
28 | ROUNI | FHGDHRF020 | 28 | ROUNI | FHGDHRF020 | 28 | ROUNI | FHGDHRF020
29 | BULANDKHERA | FHHTWAF004 | 29 | BULANDKHERA | FHHTWAF004 | 29 | BULANDKHERA | FHHTWAF004
30 | DALELGARH | FHHTWAF006 | 30 | DALELGARH | FHHTWAF006 | 30 | DALELGARH | FHHTWAF006
31 | JHALDA | FHHTWAF014 | 31 | JHALDA | FHHTWAF014 | 31 | JHALDA | FHHTWAF014
32 | KANARSI | FHHTWAF002 | 32 | KANARSI | FHHTWAF002 | 32 | KANARSI | FHHTWAF002
33 | NAWADA | FHHTWAF008 | 33 | NAWADA | FHHTWAF008 | 33 | NAWADA | FHHTWAF008
34 | BISRAKH BLOCK | FHJLPRF028 | 34 | BISRAKH BLOCK | FHJLPRF028 | 34 | BISRAKH BLOCK | FHJLPRF028
35 | AIMNABAD | FHJLPRF032 | 35 | AIMNABAD | FHJLPRF032 | 35 | AIMNABAD | FHJLPRF032
36 | Habibpur | FHJLPRF024 | 36 | Habibpur | FHJLPRF024 | 36 | Habibpur | FHJLPRF024
37 | HALDAUNI | FHJLPRF030 | 37 | HALDAUNI | FHJLPRF030 | 37 | HALDAUNI | FHJLPRF030
38 | JALPURA | FHJLPRF002 | 38 | JALPURA | FHJLPRF002 | 38 | JALPURA | FHJLPRF002
39 | Tata Motors | FHJLPRF012 | 39 | Tata Motors | FHJLPRF012 | 39 | Tata Motors | FHJLPRF012
40 | TUGALPUR MARKET | FHKPR1F004 | 40 | TUGALPUR MARKET | FHKPR1F004 | 40 | TUGALPUR MARKET | FHKPR1F004
41 | EXPRESSWAY | FHKPR2F002 | 41 | EXPRESSWAY | FHKPR2F002 | 41 | EXPRESSWAY | FHKPR2F002
42 | Haldona | FHKPR2F020 | 42 | Haldona | FHKPR2F020 | 42 | Haldona | FHKPR2F020
43 | BZP | FHLKNWF004 | 43 | BZP | FHLKNWF004 | 43 | BZP | FHLKNWF004
44 | Doob Area | FHLKNWF018 | 44 | Doob Area | FHLKNWF018 | 44 | Doob Area | FHLKNWF018
45 | KULESRA | FHLKNWF014 | 45 | KULESRA | FHLKNWF014 | 45 | KULESRA | FHLKNWF014
46 | LAKHNAWLI | FHLKNWF008 | 46 | LAKHNAWLI | FHLKNWF008 | 46 | LAKHNAWLI | FHLKNWF008
47 | MALAKPUR | FHDMASF016 | 47 | MALAKPUR | FHDMASF016 | 47 | MALAKPUR | FHDMASF016
48 | Suthyana | FHLKNWF012 | 48 | Suthyana | FHLKNWF012 | 48 | Suthyana | FHLKNWF012
49 | IMALIYAKA | FHLKSRF014 | 49 | LUKSAR | FHLKSRF002 | 49 | LUKSAR | FHLKSRF002
50 | MADHAIYA | FHST36F012 | 50 | MADHAIYA | FHST36F012 | 50 | MADHAIYA | FHST36F012
51 | AICHAR | FHST37F008 | 51 | AICHAR | FHST37F008 | 51 | AICHAR | FHST37F008
52 | MATHURAPUR | FHST37F026 | 52 | MATHURAPUR | FHST37F026 | 52 | MATHURAPUR | FHST37F026
53 | DEVLA | FHSITBF002 | 53 | DEVLA | FHSITBF002 | 53 | DEVLA | FHSITBF002
54 | Gulistanpur | FHSCSWF004 | 54 | Gulistanpur | FHSCSWF004 | 54 | Gulistanpur | FHSCSWF004
55 | DADRI ROAD TILAPTA | FHSCSWF020 | 55 | DADRI ROAD TILAPTA | FHSCSWF020 | 55 | DADRI ROAD TILAPTA | FHSCSWF020
56 | KHODNAKHURD | FHSNPRF006 | 56 | KHODNAKHURD | FHSNPRF006 | 56 | KHODNAKHURD | FHSNPRF006
57 | SAINI | FHSNPRF008 | 57 | SAINI | FHSNPRF008 | 57 | SAINI | FHSNPRF008
58 | SWARAJPUR | FHSNPRF002 | 58 | SWARAJPUR | FHSNPRF002 | 58 | SWARAJPUR | FHSNPRF002
59 | VEDPURA | FHSNPRF020 | 59 | VEDPURA | FHSNPRF020 | 59 | VEDPURA | FHSNPRF020
60 | BHANOTA | FHSNPRF024 | 60 | BHANOTA | FHSNPRF024 | 60 | BHANOTA | FHSNPRF024
61 | SUNPURA | FHSNPRF026 | 61 | SUNPURA | FHSNPRF026 | 61 | SUNPURA | FHSNPRF026
62 | BHAGAT SINGH SCHOOL | FHSRJPF030 | 62 | BHAGAT SINGH SCHOOL | FHSRJPF030 | 62 | BHAGAT SINGH SCHOOL | FHSRJPF030
63 | Lotus Park | FHSRJPF018 | 63 | Lotus Park | FHSRJPF018 | 63 | Lotus Park | FHSRJPF018
64 | SURAJPUR A & D POCKET | FHSRJPF014 | 64 | SURAJPUR A & D POCKET | FHSRJPF014 | 64 | SURAJPUR A & D POCKET | FHSRJPF014
65 | Surajpur Market | FHSRJPF022 | 65 | Surajpur Market | FHSRJPF022 | 65 | Surajpur Market | FHSRJPF022
66 | BARAHI MANDIR | FHSRJPF032 | 66 | BARAHI MANDIR | FHSRJPF032 | 66 | BARAHI MANDIR | FHSRJPF032
67 | KASHI RAM | FHXU01F002 | 67 | KASHI RAM | FHXU01F002 | 67 | KASHI RAM | FHXU01F002
68 | GHORI BHACHERA | FHXU01F010 | 68 | GHORI BHACHERA | FHXU01F010 | 68 | GHORI BHACHERA | FHXU01F010
69 | JUNPAT | FHXU01F012 | 69 | JUNPAT | FHXU01F012 | 69 | JUNPAT | FHXU01F012
70 | DABRA | FHXU03F008 | 70 | DABRA | FHXU03F008 | 70 | DABRA | FHXU03F008
71 | RITHORI | FHXU03F002 | 71 | RITHORI | FHXU03F002 | 71 | RITHORI | FHXU03F002
72 | DLF SCHOOL | FHZET1F014 | 72 | DLF SCHOOL | FHZET1F014 | 72 | DLF SCHOOL | FHZET1F014
73 | MAKORA | FHZET1F004 | 73 | MAKORA | FHZET1F004 | 73 | MAKORA | FHZET1F004
74 | MOTIPUR | FHITCTF014 | 74 | MOTIPUR | FHITCTF014 | 74 | MOTIPUR | FHITCTF014
75 | GHARBARA VILLAGE | FHITCTF016 | 75 | GHARBARA VILLAGE | FHITCTF016 | 75 | GHARBARA VILLAGE | FHITCTF016
76 | Murshadpur | FHITCTF018 | 76 | Murshadpur | FHITCTF018 | 76 | Murshadpur | FHITCTF018
77 | KULESRA COLONY | FHLKNWF022 | 77 | KULESRA COLONY | FHLKNWF022 | 77 | KULESRA COLONY | FHLKNWF022
78 | BHUDHA ROAD COLONY | FHSCSWF018 | 78 | BHUDHA ROAD COLONY | FHSCSWF018 | 78 | BHUDHA ROAD COLONY | FHSCSWF018
79 | ATAI MURADPUR | FHLKSRF016 | 79 | ATAI MURADPUR | FHLKSRF016 | 79 | ATAI MURADPUR | FHLKSRF016
80 | POVARI | FHLKSRF018 | 80 | POVARI | FHLKSRF018 | 80 | POVARI | FHLKSRF018
IF(AND(B2=B3,OR(J2=J3,L2=L3)),"Duplicate","''")
IF(AND(B2=B3,OR(J2=J3,L2=L3)),"Duplicate","''")
IFS(G3="SHUTDOWN","UPSD",G3="PLANNED OUTAGE","PSD",G3="BREAKDOWN",G3,G3="TRANSIENT FAULT",G3,G3="NO SUPPLY",G3,G3="LOAD SHEDDING",G3,G3="BREAKDOWN",G3)
IF(OR(G3>=TIME(23,0,0),G3<TIME(7,0,0)),"NIGHT",IF(AND(G3>=TIME(7,0,0),G3<TIME(15,0,0)),"MORNING",IF(AND(G3>=TIME(15,0,0),G3<TIME(23,0,0)),"EVENING", "")))
Note on B9: eco-1 ext-1 s/s
Note on AK9: eco-1 ext-1 s/s
Note on AO9: eco-1 ext-1 s/s

## TOOL ENTRIES CHECKING
TOOL FOR ENTRIES CHECKING | [19 empty] | =IF(AND(A2=A3,C2<=D3,D2>=C3),"OVERLAP",".")
COUNT |  |  | FEEDER | TOTAL | TRIP>30 MINS | REASON | TOTAL |  | TOTAL ENTRIES
DUPLICATE | 4 |  | JHALDA | 3 | 2 | 43 | 0 |  | 96
|  |  | LOAD SHEDDING | OUTAGE TIME |  | AVERAGE SUPPLY HRS |  |  | COMPARE CHARGED FEEDER
|  |  | MIN | 2:00 |  | RURAL | 21:31 |  | FEEDER | OFF HRS | COUNT
DATE | 2024-04-16 |  | MAX | 19:00 |  |  |  |  | LOTUS PARK | 0:00 | 0
[6 empty] | OUTAGE OPEN STATUS |  |  | DEVLA | 0:00 | 0
[6 empty] | 3 |  |  | .
U/D | FEEDER ID | FEEDER DESC | FEEDER TYPE | SUBSTATION | SUBSTATION DESC | OUTAGE ID | OUTAGE TYPE | STATUS | START DATE | START TIME | END DATE | END TIME | TOTAL OUTAGE TIME | AGGREGATE TIME | REASON | REASON DESCRIPTION | REMARKS | LOCATION | STAND BY FEEDER | SUBTOTAL AGG. | TRIP>30
'' | FHGDHRF026 | PATLAKHERA PTW | RURAL | SNGDHR | GIRIDHARPUR SUBSTATION | 100000001126117 | NO SUPPLY | OUTAGE CLOSED | 2024-04-16 | 3:24 | 2024-04-16 | 3:29 | 0:05 | 0:00 | C1 | 11KV SYSTEM FAILURE | SUPPLY FAILED DUE TO 11 KV I/C-1 TRIPPED AT GIRDHARPUR S/S @03:24 HRS, SCADA COMMAND FAILED. | - | NO STANDBY | 5
'' | FHLKNWF012 | SUTHYANA | RURAL URBAN | SNLKNW | LAKHNAWLI SUBSTATION | 100000001126119 | BREAKDOWN | OUTAGE CLOSED | 2024-04-16 | 4:17 | 2024-04-16 | 5:45 | 1:28 | 1:28 | 54 | CABLE TERMINATION FAILURE | HT ABC FAULT NEAR CHANDAN GYM HAS BEEN TEMPORARY RECTIFIED. | - | NO STANDBY | 88
Duplicate | FHECT2F012 | Nalagarha | AGRICULTURAL | SNECT2 | ECOTECH-2 SWITCHING CUM SUBSTATION | 100000001126193 | LOAD SHEDDING | OUTAGE OPEN | 2024-04-16 | 5:00 | 2024-04-16 | 24:00 | 19:00 | 19:00 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 1140
'' | FHECT2F012 | Nalagarha | AGRICULTURAL | SNECT2 | ECOTECH-2 SWITCHING CUM SUBSTATION | 100000001126193 | LOAD SHEDDING | OUTAGE OPEN | 2024-04-16 | 5:00 | 2024-04-16 | 24:00 | 19:00 | 19:00 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 1140
'' | FHLKNWF012 | SUTHYANA | RURAL URBAN | SNLKNW | LAKHNAWLI SUBSTATION | 100000001126118 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 5:17 | 2024-04-16 | 5:45 | 0:28 | 0:02 | 22 | BREAKDOWN ATTENDING | HT ABC FAULT NEAR CHANDAN GYM HAS BEEN TEMPORARY RECTIFIED. | KULESRA | NO STANDBY | 28
'' | FHHTWAF014 | JHALDA | RURAL | SNHTWA | HATEWA SUBSTATION | 100000001126121 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 6:14 | 2024-04-16 | 6:17 | 0:03 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | FEEDER TRIPPED AND SWITCHED ON THROUGH SCADA TRY | - | NO STANDBY | 3
'' | FHHTWAF004 | BULANDKHERA | RURAL | SNHTWA | HATEWA SUBSTATION | 100000001126124 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 6:27 | 2024-04-16 | 6:29 | 0:02 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | FEEDER TRIPPED AND SWITCHED ON THROUGH SCADA TRY | - | NO STANDBY | 2
'' | FHHTWAF006 | DALELGARH | RURAL | SNHTWA | HATEWA SUBSTATION | 100000001126126 | NO SUPPLY | OUTAGE CLOSED | 2024-04-16 | 6:27 | 2024-04-16 | 6:28 | 0:01 | 0:00 | C1 | 11KV SYSTEM FAILURE | FEEDER UNDER NO SUPPLY DUE TO HATEWA S/S 11kV I/C-2 TRIPPED ALONG BULANDKHERA FEEDER. | - | NO STANDBY | 1
'' | FHHTWAF014 | JHALDA | RURAL | SNHTWA | HATEWA SUBSTATION | 100000001126125 | NO SUPPLY | OUTAGE CLOSED | 2024-04-16 | 6:27 | 2024-04-16 | 6:28 | 0:01 | 0:00 | C1 | 11KV SYSTEM FAILURE | FEEDER UNDER NO SUPPLY DUE TO HATEWA S/S 11kV I/C-2 TRIPPED ALONG BULANDKHERA FEEDER. | - | NO STANDBY | 1
'' | FHGDHRF028 | BILASPUR TOWN | RURAL URBAN | SNGDHR | GIRIDHARPUR SUBSTATION | 100000001126123 | NO SUPPLY | OUTAGE CLOSED | 2024-04-16 | 6:27 | 2024-04-16 | 6:29 | 0:02 | 0:00 | C1 | 11KV SYSTEM FAILURE | FEEDER UNDER NO SUPPLY DUE TO 11kV BULANDKHERA FEEDER TRIPPED, AS LOAD OF BILASPUR TOWN FEEDER SHIFTED ON BULANDKHERA FEEDER DUE TO CABLE FAULT | - | NO STANDBY | 2
'' | FHHTWAF003 | HTWA 11KV INCOMER-2 | 11KV Bus Incomer | SNHTWA | HATEWA SUBSTATION | 100000001126120 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 6:27 | 2024-04-16 | 6:28 | 0:01 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | HATEWA 11kV I/C-2 TRIPPED ALONG BULANDKHERA FEEDER AND SWITCHED ON THROUGH SCADA TRY | - | NO STANDBY | 1
'' | FHST37F014 | SEC-36 S/S-3 | URBAN | SNST37 | SECTOR-37 SUBSTATION | 100000001126127 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 6:38 | 2024-04-16 | 6:41 | 0:03 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | FEEDER TRIPPED AND SWITCHED ON THROUGH SCADA TRY | - | NO STANDBY | 3
Duplicate | FHECT6F010 | D.N.V SYSTEM | INDUSTRIAL | SNECT6 | ECOTECH-6 SWITCHING CUM SUBSTATION | 100000001126128 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 6:53 | 2024-04-16 | 6:55 | 0:02 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | FEEDER TRIPPED AND SWITCHED ON THROUGH SCADA TRY | - | NO STANDBY | 2
'' | FHECT6F010 | D.N.V SYSTEM | INDUSTRIAL | SNECT6 | ECOTECH-6 SWITCHING CUM SUBSTATION | 100000001126128 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 6:53 | 2024-04-16 | 6:55 | 0:02 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | FEEDER TRIPPED AND SWITCHED ON THROUGH SCADA TRY | - | NO STANDBY | 2
'' | FHSITBF008 | SITE-C | INDUSTRIAL | SNSITB | SITE-B SUBSTATION | 100000001126136 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 6:55 | 2024-04-16 | 7:40 | 0:45 | 0:04 | 5 | OVER CURRENT & EARTH FAULT | 11kV FEEDER TRIPPED @06:55 AND NORMALIZED @07:40 . DELAY DUE TO REMOTE COMMAND FAILURE.LATER ON FEEDER SWITCHED ON LOCALLY BY CREW | - | NO STANDBY | 45 | TRIP>30
'' | FHKPR3F003 | KPR3 11kV INCOMER-2 | 11KV Bus Incomer | SNKPR3 | KP-3 SUBSTATION | 100000001126129 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 6:56 | 2024-04-16 | 6:59 | 0:03 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | KP-3 11kV I/C-2 TRIPPED ALONG JAGAT FARM FDR AND SWITCHED ON THROUGH SCADA TRY | - | NO STANDBY | 3
'' | FHKPR3F004 | FHRAI | INSTITUTIONAL | SNKPR3 | KP-3 SUBSTATION | 100000001126132 | NO SUPPLY | OUTAGE CLOSED | 2024-04-16 | 6:56 | 2024-04-16 | 6:59 | 0:03 | 0:00 | C1 | 11KV SYSTEM FAILURE | FEEDER UNDER NO SUPPLY DUE TO KP-3 11kV I/C-2 TRIPPED ALONG JAGAT FARM FEEDER. | - | NO STANDBY | 3
'' | FHKPR3F008 | JAGAT FARM | COMMERCIAL | SNKPR3 | KP-3 SUBSTATION | 100000001126135 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 6:56 | 2024-04-16 | 7:35 | 0:39 | 0:03 | 5 | OVER CURRENT & EARTH FAULT | 11kV FEEDER TRIPPED @06:56 AND NORMALIZED @07:35. DELAY DUE TO REMOTE COMMAND FAILURE.LATER ON FEEDER SWITCHED ON LOCALLY BY CREW AFTER MANUAL SPRING CHARGING. | - | NO STANDBY | 39 | TRIP>30
'' | FHKPR3F020 | IIMT COLLEGE | INSTITUTIONAL | SNKPR3 | KP-3 SUBSTATION | 100000001126131 | NO SUPPLY | OUTAGE CLOSED | 2024-04-16 | 6:56 | 2024-04-16 | 6:59 | 0:03 | 0:00 | C1 | 11KV SYSTEM FAILURE | FEEDER UNDER NO SUPPLY DUE TO KP-3 11kV I/C-2 TRIPPED ALONG JAGAT FARM FEEDER. | - | NO STANDBY | 3
'' | FHKPR3F016 | SUNSHINE (KP-3) | INSTITUTIONAL | SNKPR3 | KP-3 SUBSTATION | 100000001126130 | NO SUPPLY | OUTAGE CLOSED | 2024-04-16 | 6:56 | 2024-04-16 | 6:59 | 0:03 | 0:00 | C1 | 11KV SYSTEM FAILURE | FEEDER UNDER NO SUPPLY DUE TO KP-3 11kV I/C-2 TRIPPED ALONG JAGAT FARM FEEDER. | - | NO STANDBY | 3
'' | FHKPR1F004 | TUGALPUR MARKET | RURAL URBAN | SNKPR1 | KP-1 SUBSTATION | 100000001126133 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 7:02 | 2024-04-16 | 7:04 | 0:02 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | FEEDER TRIPPED AND SWITCHED ON THROUGH SCADA TRY | - | NO STANDBY | 2
'' | FHLKNWF018 | DOOB AREA | RURAL URBAN | SNLKNW | LAKHNAWLI SUBSTATION | 100000001126177 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 11:00 | 3:55 | 3:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 235
'' | FHITCTF014 | MOTIPUR | RURAL | SNITCT | IT CITY SWITCHING CUM SUBSTATION | 100000001126171 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHLKSRF016 | ATAI MURADPUR | RURAL | SNLKSR | LUKSAR JAIL SUBSTATION | 100000001126179 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHLKSRF014 | IMALIYAKA | RURAL | SNLKSR | LUKSAR JAIL SUBSTATION | 100000001126178 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHHTWAF008 | NAWADA | RURAL | SNHTWA | HATEWA SUBSTATION | 100000001126169 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHJLPRF032 | AIMNABAD | RURAL URBAN | SNJLPR | JALPURA SUBSTATION | 100000001126175 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHHTWAF014 | JHALDA | RURAL | SNHTWA | HATEWA SUBSTATION | 100000001126170 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHSNPRF002 | SWARAJPUR | RURAL | SNSNPR | SUNPURA SUBSTATION | 100000001126181 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 11:00 | 3:55 | 3:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 235
'' | FHJLPRF028 | BISRAKH BLOCK | RURAL URBAN | SNJLPR | JALPURA SUBSTATION | 100000001126174 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHLKNWF008 | LAKHNAWLI | RURAL URBAN | SNLKNW | LAKHNAWLI SUBSTATION | 100000001126176 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHSNPRF006 | KHODNAKHURD | RURAL | SNSNPR | SUNPURA SUBSTATION | 100000001126182 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:30 | 3:25 | 3:25 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 205
'' | FHLKSRF018 | POVARI | RURAL | SNLKSR | LUKSAR JAIL SUBSTATION | 100000001126180 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHITCTF016 | GHARBARA VILLAGE | RURAL | SNITCT | IT CITY SWITCHING CUM SUBSTATION | 100000001126172 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHSNPRF008 | SAINI | RURAL | SNSNPR | SUNPURA SUBSTATION | 100000001126183 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:30 | 3:25 | 3:25 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 205
'' | FHITCTF018 | MURSHADPUR | RURAL | SNITCT | IT CITY SWITCHING CUM SUBSTATION | 100000001126173 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHEC11F010 | MAICHA | RURAL | SNEC11 | ECOTECH-11 SUBSTATION | 100000001126159 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHEC11F008 | LADPURA | RURAL | SNEC11 | ECOTECH-11 SUBSTATION | 100000001126158 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHEC11F006 | GHANGHOLA | RURAL | SNEC11 | ECOTECH-11 SUBSTATION | 100000001126157 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHEC11F010 | MAICHA | RURAL | SNEC11 | ECOTECH-11 SUBSTATION | 100000001126159 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHEC11F008 | LADPURA | RURAL | SNEC11 | ECOTECH-11 SUBSTATION | 100000001126158 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHEC11F006 | GHANGHOLA | RURAL | SNEC11 | ECOTECH-11 SUBSTATION | 100000001126157 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHXU03F002 | RITHORI | RURAL | SNXU03 | XU-3 SWITCHING CUM SUBSTATION | 100000001126190 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHXU03F008 | DABRA | RURAL | SNXU03 | XU-3 SWITCHING CUM SUBSTATION | 100000001126191 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHXU01F012 | Junpat | RURAL | SNXU01 | XU-1 SUBSTATION | 100000001126189 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHXU01F002 | Kashi Ram | RURAL URBAN | SNXU01 | XU-1 SUBSTATION | 100000001126187 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHXU01F010 | Ghori Bhachera | RURAL | SNXU01 | XU-1 SUBSTATION | 100000001126188 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHHTWAF004 | BULANDKHERA | RURAL | SNHTWA | HATEWA SUBSTATION | 100000001126167 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHGDHRF026 | PATLAKHERA PTW | RURAL | SNGDHR | GIRIDHARPUR SUBSTATION | 100000001126164 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:30 | 3:25 | 3:25 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 205
'' | FHZET1F004 | MAKORA | RURAL | SNZET1 | ZETA-1 SWITCHING CUM SUBSTATION | 100000001126192 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 11:00 | 3:55 | 3:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 235
'' | FHHTWAF002 | KANARSI | RURAL | SNHTWA | HATEWA SUBSTATION | 100000001126166 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHSNPRF020 | VEDPURA | RURAL | SNSNPR | SUNPURA SUBSTATION | 100000001126184 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:30 | 3:25 | 3:25 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 205
'' | FHGDHRF024 | PANCHAYTAN | RURAL | SNGDHR | GIRIDHARPUR SUBSTATION | 100000001126163 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:30 | 3:25 | 3:25 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 205
'' | FHSNPRF026 | SUNPURA | RURAL | SNSNPR | SUNPURA SUBSTATION | 100000001126186 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:30 | 3:25 | 3:25 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 205
'' | FHGDHRF028 | BILASPUR TOWN | RURAL URBAN | SNGDHR | GIRIDHARPUR SUBSTATION | 100000001126165 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHSNPRF024 | BHANOTA | RURAL | SNSNPR | SUNPURA SUBSTATION | 100000001126185 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:30 | 3:25 | 3:25 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 205
'' | FHHTWAF006 | DALELGARH | RURAL | SNHTWA | HATEWA SUBSTATION | 100000001126168 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:05 | 2024-04-16 | 10:00 | 2:55 | 2:55 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 175
'' | FHCHI4F006 | MOMNATHAL | RURAL URBAN | SNCHI4 | CHI-4 SWITCHING CUM SUBSTATION | 100000001126155 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:10 | 2024-04-16 | 10:00 | 2:50 | 2:50 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 170
'' | FHSW02F008 | KHERPUR GUJJAR | RURAL | SNSW02 | ESS-2 SWITCHING CUM SUBSTATION | 100000001126156 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:10 | 2024-04-16 | 10:00 | 2:50 | 2:50 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 170
'' | FHCHI4F002 | CHUHARPUR KHADAR | RURAL URBAN | SNCHI4 | CHI-4 SWITCHING CUM SUBSTATION | 100000001126154 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:10 | 2024-04-16 | 10:00 | 2:50 | 2:50 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 170
'' | FHSITBF014 | SHYAM PIPE | INDUSTRIAL | SNSITB | SITE-B SUBSTATION | 100000001126134 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 7:11 | 2024-04-16 | 7:17 | 0:06 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | FEEDER TRIPPED AND SWITCHED ON THROUGH SCADA TRY | - | NO STANDBY | 6
Duplicate | FHECT2F002 | Tubewell Branch | AGRICULTURAL | SNECT2 | ECOTECH-2 SWITCHING CUM SUBSTATION | 100000001126153 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:30 | 2024-04-16 | 12:48 | 5:18 | 5:18 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 318
'' | FHECT2F002 | Tubewell Branch | AGRICULTURAL | SNECT2 | ECOTECH-2 SWITCHING CUM SUBSTATION | 100000001126153 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 7:30 | 2024-04-16 | 12:48 | 5:18 | 5:18 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 318
'' | FHLKSRF012 | ATEN FOODS | INDUSTRIAL | SNLKSR | LUKSAR JAIL SUBSTATION | 100000001126137 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 7:41 | 2024-04-16 | 7:51 | 0:10 | 0:01 | 5 | OVER CURRENT & EARTH FAULT | 11kV FEEDER TRIPPED @07:41 AND NORMALIZED @07:51 THROUGH REMOTE COMMAND | - | NO STANDBY | 10
'' | FEECT2F014 | GLOBAL AUTO TECH | 33kV BRANCH FEEDER-INDUSTRIAL | SNECT2 | ECOTECH-2 SWITCHING CUM SUBSTATION | 100000001126138 | PLANNED OUTAGE | OUTAGE CLOSED | 2024-04-16 | 7:58 | 2024-04-16 | 8:10 | 0:12 | 0:01 | 98 | METERING WORK | CONSUMER ISOLATED FOR METERING TEAM INSTALLED METERING CUBICAL FOR 33kV CONSUMER-GLOBAL AUTO TECH CONVERTED IN OPEN ACCESS. METERING TEAM WORK-PUNIT & VIKRAM JI. | Global Autotech Consumer' Fusing Reconnection | NO STANDBY | 12
'' | FHCONRF016 | TILAPTA CANAL | RURAL URBAN | SNCONR | CONTAINER CORPORATION SUBSTATION | 100000001126149 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 8:00 | 2024-04-16 | 10:00 | 2:00 | 2:00 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 120
'' | FHECTCF014 | KHANPUR | RURAL URBAN | SNECTC | ECOTECH EXTENSION-1 SUBSTATION | 100000001126150 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 8:00 | 2024-04-16 | 10:00 | 2:00 | 2:00 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 120
'' | FHCONRF004 | SANTOSH NAGAR | RURAL URBAN | SNCONR | CONTAINER CORPORATION SUBSTATION | 100000001126148 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 8:00 | 2024-04-16 | 10:00 | 2:00 | 2:00 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 120
'' | FHECTCF014 | KHANPUR | RURAL URBAN | SNECTC | ECOTECH EXTENSION-1 SUBSTATION | 100000001126150 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 8:00 | 2024-04-16 | 10:00 | 2:00 | 2:00 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 120
'' | FHSCSWF020 | DADRI ROAD TILAPTA | RURAL URBAN | SNSCSW | SITE-C SWITCHING CUM SUBSTATION | 100000001126152 | LOAD SHEDDING | OUTAGE CLOSED | 2024-04-16 | 8:00 | 2024-04-16 | 10:00 | 2:00 | 2:00 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 120
'' | FHJLPRF012 | TATA MOTORS | RURAL URBAN | SNJLPR | JALPURA SUBSTATION | 100000001126139 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 8:08 | 2024-04-16 | 8:13 | 0:05 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | 11kV FEEDER TRIPPED @08:08 AND NORMALIZED @08:13 THROUGH REMOTE COMMAND | - | NO STANDBY | 5
'' | FHST37F008 | AICHAR | RURAL URBAN | SNST37 | SECTOR-37 SUBSTATION | 100000001126140 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 8:39 | 2024-04-16 | 9:04 | 0:25 | 0:02 | 21 | COMPLAINT ATTENDING | HT FUSE RECTIFIED FROM TXR-8341/250kVA NEAR MASJID WALI GALI AICHER | MASJID WALI GALI AICHER | NO STANDBY | 25
'' | FHUDKRF026 | INNOTECH | INDUSTRIAL | SNUDKR | UDYOG KENDRA SUBSTATION | 100000001126142 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 8:48 | 2024-04-16 | 8:50 | 0:02 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | FDR TRIPPED@08:48 AND NORMALIZED@08:50 AFTER TRY THROUGH SCADA. | - | NO STANDBY | 2
'' | FHKPR2F002 | EXPRESSWAY | AGRICULTURAL | SNKPR2 | KP-2 SUBSTATION | 100000001126147 | LOAD SHEDDING | OUTAGE OPEN | 2024-04-16 | 9:15 | 2024-04-16 | 24:00 | 14:45 | 14:45 | 40 | SUPPLY RESTRICTION |  |  | NO STANDBY | 885
'' | FHSITBF008 | SITE-C | INDUSTRIAL | SNSITB | SITE-B SUBSTATION | 100000001126141 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 9:29 | 2024-04-16 | 9:46 | 0:18 | 0:01 | 21 | COMPLAINT ATTENDING | HT FUSE ROM DP:17515 | B 21 SITE C | NO STANDBY | 18
'' | FHLKNWF004 | BZP | RURAL URBAN | SNLKNW | LAKHNAWLI SUBSTATION | 100000001126145 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 9:45 | 2024-04-16 | 10:25 | 0:40 | 0:04 | 21 | COMPLAINT ATTENDING | LT ACBLE RECTIFIED | NEAR DIG FARM | NO STANDBY | 40
'' | FHLKNWF014 | KULESRA | RURAL URBAN | SNLKNW | LAKHNAWLI SUBSTATION | 100000001126144 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 9:48 | 2024-04-16 | 9:53 | 0:05 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | FDR TRIPPED@09:48 AND NORMALIZED@09:53 AFTER TRY THROUGH SCADA. | - | NO STANDBY | 5
'' | FHXU01F012 | Junpat | RURAL | SNXU01 | XU-1 SUBSTATION | 100000001126143 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 9:53 | 2024-04-16 | 9:56 | 0:03 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | FDR TRIPPED@09:53 AND NORMALIZED@09:56 AFTER TRY THROUGH SCADA. | - | NO STANDBY | 3
Duplicate | FHECT6F022 | KASNA VILLAGE | RURAL URBAN | SNECT6 | ECOTECH-6 SWITCHING CUM SUBSTATION | 100000001126203 | PLANNED OUTAGE | OUTAGE CLOSED | 2024-04-16 | 10:47 | 2024-04-16 | 13:49 | 3:02 | 3:02 | 96 | LCC WORK | LCC TEAM WORK DONE | kasna village | NO STANDBY | 182
'' | FHECT6F022 | KASNA VILLAGE | RURAL URBAN | SNECT6 | ECOTECH-6 SWITCHING CUM SUBSTATION | 100000001126203 | PLANNED OUTAGE | OUTAGE CLOSED | 2024-04-16 | 10:47 | 2024-04-16 | 13:49 | 3:02 | 3:02 | 96 | LCC WORK | LCC TEAM WORK DONE | kasna village | NO STANDBY | 182
'' | FHSNPRF006 | KHODNAKHURD | RURAL | SNSNPR | SUNPURA SUBSTATION | 100000001126197 | PLANNED OUTAGE | OUTAGE CLOSED | 2024-04-16 | 10:55 | 2024-04-16 | 12:45 | 1:50 | 1:50 | 96 | LCC WORK | LCC WORK | KHODNA KHURD | NO STANDBY | 110
'' | FHCHI4F014 | CHI-4 PUMP | PUMP | SNCHI4 | CHI-4 SWITCHING CUM SUBSTATION | 100000001126146 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 11:00 | 2024-04-16 | 11:09 | 0:09 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | 11kV FEEDER TRIPPED @11:00 AND NORMALIZED @11:09 THROUGH REMOTE COMMAND | - | NO STANDBY | 9
'' | FHST37F008 | AICHAR | RURAL URBAN | SNST37 | SECTOR-37 SUBSTATION | 100000001126198 | PLANNED OUTAGE | OUTAGE CLOSED | 2024-04-16 | 11:04 | 2024-04-16 | 12:52 | 1:48 | 1:48 | 96 | LCC WORK | LCC WORK | Aichar | NO STANDBY | 108
'' | FHSW10F006 | Khera Chauganpur | RURAL URBAN | SNSW10 | ESS-10 SWITCHING CUM SUBSTATION | 100000001126207 | PLANNED OUTAGE | OUTAGE CLOSED | 2024-04-16 | 11:12 | 2024-04-16 | 14:35 | 3:23 | 3:23 | A5 | TREE PRUNING | TREE PURNING DONE | Kherachauganpur | NO STANDBY | 203
'' | FHXU01F006 | XU-2 | URBAN | SNXU01 | XU-1 SUBSTATION | 100000001126194 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 11:25 | 2024-04-16 | 11:29 | 0:04 | 0:00 | 5 | OVER CURRENT & EARTH FAULT | 11kV FEEDER TRIPPED @11:25 AND NORMALIZED @11:29 THROUGH REMOTE COMMAND | - | NO STANDBY | 4
'' | FHSITBF008 | SITE-C | INDUSTRIAL | SNSITB | SITE-B SUBSTATION | 100000001126195 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 11:33 | 2024-04-16 | 11:51 | 0:19 | 0:01 | 21 | COMPLAINT ATTENDING | HT FUSE TXR RECTEFIED TXR NO-6153 25 KVA | F-02,SITE-C | NO STANDBY | 19
'' | FHE3P2F010 | WYBOR TECH | INDUSTRIAL | SNE3P2 | ECOTECH-3 PHASE-2 SUBSTATION | 100000001126196 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 11:40 | 2024-04-16 | 11:56 | 0:16 | 0:01 | 21 | COMPLAINT ATTENDING | HT FUSE DP RECTEFIED DP NO-04226 | PLOT NO.H-347 UK-2 | NO STANDBY | 16
'' | FHLKNWF014 | KULESRA | RURAL URBAN | SNLKNW | LAKHNAWLI SUBSTATION | 100000001126210 | BREAKDOWN | OUTAGE CLOSED | 2024-04-16 | 12:24 | 2024-04-16 | 13:22 | 0:58 | 0:05 | 54 | CABLE TERMINATION FAILURE | HT TERMINATION FAULT NEAR SUNDAY MARKET, 80 % LOAD OF FEEDER WAS RESTORED @12:27 | - | NO STANDBY | 58
'' | FHSTR2F018 | SECTOR-1 | URBAN | SNSTR2 | SECTOR-2 SUBSTATION | 100000001126205 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 12:32 | 2024-04-16 | 13:55 | 1:23 | 1:23 | 37 | SAFETY/EMERGENCY | JUMPER RECTEFIED POLE OD -47148 | NEAR PARAMOUNT SOCIETY SEC 01 | NO STANDBY | 83
'' | FHLKNWF014 | KULESRA | RURAL URBAN | SNLKNW | LAKHNAWLI SUBSTATION | 100000001126202 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 12:38 | 2024-04-16 | 13:22 | 0:45 | 0:04 | 22 | BREAKDOWN ATTENDING | HT ABC TERMINATION FAULT, TEMPORARY RECTIFIED. | NEAR SUNDAY MARKET KULESRA | NO STANDBY | 45
'' | FHHTWAF002 | KANARSI | RURAL | SNHTWA | HATEWA SUBSTATION | 100000001126200 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 12:50 | 2024-04-16 | 13:12 | 0:22 | 0:02 | 21 | COMPLAINT ATTENDING | LT ABC RECTIFIED | CHACHULA VILLAGE | NO STANDBY | 22
'' | FHLKNWF004 | BZP | RURAL URBAN | SNLKNW | LAKHNAWLI SUBSTATION | 100000001126204 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 13:31 | 2024-04-16 | 13:53 | 0:22 | 0:02 | 21 | COMPLAINT ATTENDING | HT FUSE TXR RECTEFIED TXR NO-7352 100 KVA | MUBARAKPUR VILLAGE | NO STANDBY | 22
'' | FHUDKRF026 | INNOTECH | INDUSTRIAL | SNUDKR | UDYOG KENDRA SUBSTATION | 100000001126206 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 13:48 | 2024-04-16 | 14:04 | 0:16 | 0:01 | 21 | COMPLAINT ATTENDING | HT FUSE DP RECTEFIED DP NO-06054 | PLOT NO-8/A UK-1 | NO STANDBY | 16
'' | FHZET1F004 | MAKORA | RURAL | SNZET1 | ZETA-1 SWITCHING CUM SUBSTATION | 100000001126208 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 14:13 | 2024-04-16 | 14:38 | 0:25 | 0:02 | 21 | COMPLAINT ATTENDING | LT ABC RECTEFIED IN PALI VILLAGE | PALI | NO STANDBY | 25
'' | FHCHI4F014 | CHI-4 PUMP | PUMP | SNCHI4 | CHI-4 SWITCHING CUM SUBSTATION | 100000001126211 | SHUTDOWN | OUTAGE CLOSED | 2024-04-16 | 14:37 | 2024-04-16 | 14:55 | 0:18 | 0:01 | 22 | BREAKDOWN ATTENDING | JUMPER OPEN GBU UNIVERSITY ROAD | GBU UNIVERSITY ROAD | NO STANDBY | 18
| FHUDKRF010 | RAHUL | INDUSTRIAL | SNUDKR | UDYOG KENDRA SUBSTATION | 100000001126212 | TRANSIENT FAULT | OUTAGE CLOSED | 2024-04-16 | 14:39 | 2024-04-16 | 14:51 | 0:12 | 0:01 | 5 | OVER CURRENT & EARTH FAULT | FDR TRIPPED@14:39 AND NORMALIZED@14:51 AFTER MANUAL TRY DUE TO CB STATUS BAD. | - | NO STANDBY | 12
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## REMARKS REF...
REMARKS REFERENCES
REASON | SUB/REASON | * | REMARKS
B/D | GI/OFC | * | THE FEEDER BREAKDOWN @ (TIME). AFTER PATROLLING, NO FAULT WAS FOUND. THE CREW TRIED, BUT THE FEEDER DIDN'T HOLD. POWER WAS THEN TEMPORARILY RESTORED TO SOME AREAS BY BACKFEEDING FROM THE 11KV FEEDER, ORIGINATING FROM THE RMU NEAR (LOCATION). THE REST WAS PATROLLED, AND A FIBER WIRE WAS FOUND TOUCHING A DROPPED POINT NEAR -C112. AFTER REMOVING IT, THE FEEDER NORMALIZED, AND POWER WAS RESTORED @ (TIME).
B/D | GI/OFC | * | THE FEEDER WENT UNDER BREAKDOWN @( ). AFTER PATROLLING, NO FAULTS WERE FOUND. THE CREW ATTEMPTED TO RECTIFY THE ISSUE, BUT THE FEEDER DID NOT HOLD. CONSEQUENTLY, POWER WAS TEMPORARILY RESTORED TO SOME AREAS BY BACKFEEDING FROM THE 11KV FEEDER, ORIGINATING FROM THE RMU NEAR ( ). THE REMAINING AREA WAS PATROLLED, AND A FIBER WIRE WAS FOUND TOUCHING A DROPPED POINT NEAR -C112. AFTER REMOVING THE FIBER WIRE, THE FEEDER NORMALIZED, AND POWER WAS RESTORED @( ).
B/D | GI/OFC | * | THE CRADLE GUARD'S GI WIRE TOUCHED THE CONDUCTOR NEAR- , AFTER RECTIFYING THE ISSUE, THE FDR NORMALIZED @( ).
B/D | NO FAULT | * | THE FEEDER WENT UNDER BREAKDOWN @( ). AFTER PATROLLING, NO FAULTS WERE FOUND.
B/D | 33 KV NO FAULT | * | RC#01 TRIPPED WITH 7kA AMPERE FAULT CURRENT IN R&Y PHASE,RC GREEN S/S DECLARED BREAKDOWN. AFTER PATROLING NO FAULT FOUND THEN RC#01 CKT BACKFEEDED BY F#8 FROM ECOTECH-03 PHASE-02 S/S YARD. FINALLY FEEDER NORMALISED AT 15:40 HRS. LOAD AFFECTED T
B/D | 11 KV I/C NO FAULT | * | 11KV I/C-2 TRIPPED WITH JALPURA FDR. I/C-2 NORMALIZED AFTER TRY VIA REMOTE OPERATION COMMAND. JALPURA FDR DELCEARED IN BREAKDOWN FROM @12:35HRS, LINE PATROLING DONE AFTER SECTION WISE TRY FDR NORMALIZED@14:35HRS. NO FAULT FOUND.
B/D | 33 KV NO FAULT | * | RC#09 TRIP WITH 60MVA P.TXR-1&2 AT RC GREEN S/S WITH A FAULT CURRENT OF 13KA & 7KA IN R& Y-PHASE RESP, AFFECTED LOAD RESTORED TILL 01:33 AFTER CHANGEOVER, MEGGERING AND BACKFEEDING DONE SUCCESFULLY OF ALL SECTIONS AND NORMALISED @07:14 HRS
B/D | 33 KV NO FAULT | * | FEEDR UNDER BREAKDOWN@18:18, NO FAULT FOUND DURING LINE PATROLLING. RC#15 CKT BACKFEEDE BY RC#03 & LLD TEST FOUND OK AND FEEDER NORMALISED@21:10
B/D | 11 KV NO FAULT | * | 11 KV FEEDER NAWADA DECLARED UNDER B/D @17:50 HRS AFTER A TRY, AFTER PATROLLING FOR FAULT IDENTIFICATION A TRY IS TAKEN THROUGH SCADA WHEN NO VISIBLE FAULT WAS FOUND AND FEEDER HOLD @18:20HRS
B/D | 11 KV BIRD FAULT | * | 11KV ECDM TECHNOLOGY FDR TRIPPED @ 14:25HRS AND C.B. WAS NOT CLOSED THROUGH ETAP LATER B\D CREW HAVE TAKEN SECTIONWISE TRY THROUGH RMU NEAR PLOT NO.154,UK-2,RMU OG-1 LOAD NORMALISED @ 15:00HRS.SQUIRREL DIED FOUND AT PLOT NO. 347D,E-3P-2
B/D | 33 KV BIRD FAULT | * | F#07 TRIPPED AT 08:14 HRS WITH 6KA F/C IN Y-PHASE. LOAD OF POWER TXR-2 AT SITE-B S/S C/O ON RC#23 BY SHIFT ENGINEER AT 08:32 HRS. AFTER PATROLING BIRD FAULT FOUND NEAR LOTUS SOCIETY SURAJPUR, LINE CLEARED. F#07 NORMALISED AFTER TRY AT 09:14 HRS
B/D | 33 KV BIRD FAULT | * | FDR TRIPPED@07:45 WITH 5kmp IN R-PHASE AFTER PATROLLING OF CIRCUIT MONKEY ELECTROCUTED FOUND ON 33 KV LINE NEAR BY DHARAMPAL MARKET. BROKEN GUARD WIRE AND MONKEY REMOVED.AND AFTER THIS FDR NORMALISED@09:04
B/D | 11 KV CABLE DAMAGE | * | CABLE CUT NY NPCL PROJECT TEAM, LOAD SHIFTED ON HR INDUSTRIES THROUGH JUMPER NEAR Q-25 SITE-5.
B/D | 33 KV CABLE DAMAGE | * | RC#17 FDR BREAKDOWN DUE TO CABLE DAMAGED BY FIRE CASE ,33KV O&M TEAM TOOK THE S/D AND ISOLATOR OPEN NEAR TILAPTA ROTARY,RC#17 CKT ARE NOT REACHING ESS-10 AND ESS-2 S/S.
B/D | 33 KV CABLE DAMAGE | * | FDR UNDER BD FROM 11:18 AFTER PATROLING SHIFT ER. INFOREMED THAT FIRE IN HT CABLE NEAR ACCURATE COLLEGE KP-2, FIRE EXTINGUISHED AND BURNT END TERMINATION RECTIFIED AND FDR NORMALIZED@11:00 ON DATED 13-03-2024.
B/D | CABLE FAULT | * | HT ABC SUSPECTED CABLE FAULT NEAR BY BETWEEN SEC 2 S/S- SEC 16 PKT S/S, LOAD SHIFTED ON SEC 3 C & D PKT FDR.
B/D | NO FAULT | * | FEEDER UNDER BREAKDOWN DECLARED @09:30 AND NORMALIZED @11:08. NO FAULT FOUND. FEEDER NORMALIZED AFTER PATROLLING
B/D | CABLE DAMAGE | * | BREAKDOWN: SUBSTATION PANEL TO CONSUMER RMU CABLE BEING DAMAGED BY A JCB. WHEN THE CONSUMER LOAD WAS ATTEMPTED TO BE TRANSFERRED TO ANOTHER 11KV INCOMING CIRCUIT (BHAGWATI), THE RMU OG BRANCH TRIPPED AS A RESULT. AFTER PERFORMING A TEST ON THE
B/D | CONDUCTOR SNAP | * | SUNLAC PAINTS FDR TRIPPED @13:13 AFTER TRY DECLARED UNDER B/D @13:30,ALL FUSE BLOWN OF PLOT NO 95, ECO-1 EXT, NORMALISED @17:15 HRS.
B/D | CONDUCTOR SNAP | * | FEEDER UNDER B/D FROM 18:23 DUE TO CONDUCTOR SLIPPED FROM PIN AND TOUCHED TO CHANNEL ON POLE ID-36800 THEN FAULT RECTIFIED AND FEEDER NORMALISED @01:30 (30.03.2024)
B/D | FAULT AT CONSUMER END | * | FEEDER UNDER BREAKDOWN DUE TO ALL FUSE BLOWN OUT OF SAMRIDHI,GH-09,TECHZONE-4,B.P-2000229250, FAULT AT CONSUMER SIDE,ISOLATED CASE FORWARDED IN TESTING
B/D | JUMPER BLOWN | * | BREAKDOWN –FEEDER TRIPPED AT 15:00 HRS., AND NORMALIZED AFTER TRY AT 05:31 BUT FEEDER WAS UNDER SINGLE PHASING AFTER SWITCH ON BECAUSE OF THAT THE LOAD OF SITE-B SUBSTATION WAS AFFECTED FROM 15:00-16:11 HRS., THE LOAD CHANGEOVER FOR SITE-B SUBS
B/D | JUMPER BLOWN | * | AFTER PATROLLING HT JUMPER BLOWN FOUND ON ISOLATOR AT SURAJPUR S/S, FEEDRER LOAD RESTORED AFTER HT JUMPER RECTIFICATION.
B/D | 33 KV NO FAULT | * | FDR TRIPPED @ 23:47 ON DATED 28-3-24 WITH 7K.A FAULT IN Y AND B PHASE AND FDR DECLARED BREAKDOWN AFTER PATROLLING NO FAULT FOUND.THEN BACKFEEDING DONE ON FD#09 AND FDR HELD.THEN FD#5 NORMALISED @02:01 DATE 29-03-24
B/D | 11 KV BIRD FAULT | * | 11KV I/C-2 TRIPPED ALONG WITH 11KV 32PI PUMP FDR@17:00. 11KV I/C-2 NORMALIZED @17:03. 32PI-PUMP FDR UNDER BD, SAME INFORMED TO SHIFT ENGINEER. AFTER PATROLLING SQUIRREL FOUND ELECTROCUTED NEAR TXR-6411. FDR NORMALIZED AFTER TRY @17:25.
B/D | EQUIPMENTS DAMAGE (OTHERS) | * | FDR UNDER BREAKDOWN DUE TO FIRE CASE AT COMPOSITE CT PT. RMU I/C SWITCHED OFF AND CKT SWITCH ON AT NO-LOAD@ 17:20HRS. SHUTDOWN TAKEN FROM RMU(NEAR CRPF CAMP)AND ISOALTE THE FAULTY CT PT AND DUE TO THIS 1-NOS 100KVA TXR/3687 AFFECTED(STREET LIG
B/D | 11 KV NO FAULT | * | 11kV FEEDER UNDER BREAKDOWN @12:07 AND NORMALIZED @12:56. SECTION WISE TRY ISOLATING RMUs. NO FAULT FOUND. FEEDER SWITCHED ON LOCALLY BY CREW
B/D | PANEL PROBLEM | * | FDR UNDER BD FROM 11:18 AFTER PATROLING SHIFT ER. INFOREMED THAT FIRE IN HT CABLE NEAR ACCURATE COLLEGE KP-2, FIRE EXTINGUISHED AND BURNT END TERMINATION RECTIFIED AND FDR NORMALIZED@11:00 ON DATED 13-03-2024.
B/D | PANEL PROBLEM | * | FDR HAVE SPRING CHARGING ISSUE CONFIRMED BY CEW AND DUE TO THIS FDR NOT SWITCH ON VIA SCADA. SWITCHED ON MANUALLY BY CREW AND SUPPLY NORMALIZED @ 13:25.
B/D | TREE FALLEN | * | FEEDER UNDER B/D FROM @18:14 DUE TO TREE BRANCH FALLEN ON MAIN LINE NEAR B-1 SITE-4, FEEDER NORMALIZED @19:33 AFTER REMOVING FALLEN TREE BRANCH BY B/D CREW.
TRANSIENT FAULT | OVER CURRENT & EARTH FAULT | * | FDR TRIPPED@05:39 AND NORMALIZED@05:41 AFTER TRY BY REMOTE OPERATION COMMAND.
TRANSIENT FAULT | THUNDERSTORM | * | FEEDER TRIPPED @18:17 AND NORMALISED @19:02 DELAY DUE TO RAIN AND STORM
TRANSIENT FAULT | OVER CURRENT & EARTH FAULT | * | FEEDER TRIPPED @11:05 AFTER THIS CONTROL ROOM TAKE TRY @11:13 BY ETAP ,CONTROL FAILED AND AFTER THIS MANUAL TRY FEEDER RESTORE @ 11:34
TRANSIENT FAULT | 33kV FDR TRIPPED | * | IMPORT FEEDER FD#05 FROM SURAJPUR 132kV S/S TRIPPED WITH 4.4kA EARTH FAULT OVER CURRENT IN R-PHASE; AFTER NO LOAD TRY FDR LOAD RESTORED SUCCESSFULLY @19:05.AFFECTED LOAD- JALPURA S/S & LAKHNAWALI S/S (WHICH WAS SHIFTED DUE TO FD#08 B/D)
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.